## EFA PSBP Front Page
Distance to reach fully turbulent flow | 0 | m | set this to be zero if you want to allow entrainment to start as soon as air enters the room - this is the most optimistic assumption possible for a window
INPUTS
Width of opening window or damper | 5 | m
Average temperature of classroom | 21 | C
Height from floor to top of opening window/damper | 2.7 | m
Vertical extent of opening high level window/damper | 0.4 | m
Select high-level opening type | Top hung window
Number of occupants | 32
Minimum fresh air rate per person | 5 | l/s
RESULTS
Primary School (1.1m) | Pass
Secondary School (1.4m) | Fail
This spreadsheet tool is based on standard plume theory from Turner (1973), Buoyancy Effects in Fluids. It also uses the concept of a virtual origin for plumes following the work of Kaye & Hunt. It shows how the temperature of an incoming stream of cold air through a high level window or damper into a warm room increases as the turbulent plume falls under gravity and entrains warm room air. The entrainment is just from one side of the line plume since the other side is against the window.
When the temperature of the plume 1.4m from the floor (given by the light blue line for secondary schools) or 1.1m from the floor (given by the dark blue line for primary schools) is below the minimum acceptable level for schools (given by the red line) for any external temperature above 5C (denoted by the dotted black line), the system FAILS to meet the criterion for draughts as laid out in BB101 2018, which is that the temperature needs to be within 5C of the ambient temperature for all external temperatures above 5C.
When the temperature of the plume (blue lines) is above the minimum temperature (red line), the system PASSES the criterion for cold draughts.
The model assumes that the flow is fully turbulent the moment air enters the room. This is the most optimistic assumption with regards to the effectiveness of mixing. Note that the effects of gusts are also not accounted for. Finally, although entrainment is modelled only from one side of the plume, the reduced turbulence arising from the fact that the plume is constrained by a solid boundary is also not included. The modelling results therefore indicate an optimistic view of the mixing effectiveness and colder temperatures at the occupied level may be experienced.
The results should be interpreted as follows:
1) If the temperatures predicted show a FAIL then it is very likely that draughts will be a serious issue in your design and alternative solutions are recommended.
2) If the temperatures predicted show a PASS then the designer can proceed, but note that the results do not guarantee draught free conditions at all times. If completely draught free conditions are desired under all weather conditions then alternative ventilation solutions should be pursued.
For more information please see www.breathingbuildings.com
Furthermore, if anyone wishes to obtain the full calculations in the spreadsheet please contact info@breathingbuildings.com
This spreadsheet tool is free for designers to use to help them in the assessment of the most appropriate openings for wintertime ventilation.
The entrainment coefficient for turbulent plumes is usually taken to be 0.102. However, following work undertaken by Prof Malcolm Cook (Loughborough University), Prof Paul Linden, David Parker and Prof Colm-cille Caulfied (University of Cambridge), and discussions with Dr Henry Burridge (Imperial College), Dr Connick (Breathing Buildings) and Dr Shaun Fitzgerald (University of Cambridge and Breathing Buildings) regarding a line plume against a solid boundary, it has been recommended that the coefficient be 0.08 and this value is therefore used.
Use of the tool in other applications
This simple tool can be used to help investigate some other scenarios. If a designer wishes to assess the entrainment as a result of uni-directional inflow through a horizontal damper in a space, then the flow can be approximated to leading order as a line plume emanating from all 4 sides of the damper. So, if the damper is 1.5m x 1.5m, the length of the window/damper should be given as 4x1.5m = 6m. The critical height is the height from the floor to the point at which mixing starts. It is easiest to state that the opening is a bottom hung window, and ensure that the height from the floor to the top of the opening in this model is then simply the height from the floor to the point where mixing can commence, which is usually at ceiling level.

## calcs (hidden)
SECONDARY SCHOOLS
alpha T | 0.08 | (standard value would be 0.102 but following discussion with Malcolm Cook in Dec 2016, and subsequent discussions with Paul Linden, Malcolm Cook, Henry Burridge, David Parker, Colm-cille Caulfield, Owen Connick and Shaun Fitzgerald in Mar 2018 it was agreed this should be reduced to 0.08)
C | 0.085668 | (not used)
Vl source | 0.032 | cu m/s/m
T ext | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3
g prime source | 0.1962 | 0.2289 | 0.2616 | 0.2943 | 0.327 | 0.3597 | 0.3924 | 0.4251 | 0.4578 | 0.4905 | 0.5232 | 0.5559 | 0.5886 | 0.6213 | 0.654 | 0.6867 | 0.7194 | 0.7521 | 0.7848
Bo | 0.0075341 | 0.0087898 | 0.010045 | 0.011301 | 0.012557 | 0.013812 | 0.015068 | 0.016324 | 0.01758 | 0.018835 | 0.020091 | 0.021347 | 0.022602 | 0.023858 | 0.025114 | 0.026369 | 0.027625 | 0.028881 | 0.030136
h virtual origin | 0.66273 | 0.62957 | 0.60219 | 0.57903 | 0.55906 | 0.5416 | 0.52613 | 0.51229 | 0.4998 | 0.48845 | 0.47807 | 0.46851 | 0.45968 | 0.45148 | 0.44383 | 0.43668 | 0.42997 | 0.42365 | 0.41769
g prime floor | 0.083444 | 0.09448 | 0.10516 | 0.11553 | 0.12563 | 0.1355 | 0.14515 | 0.1546 | 0.16388 | 0.173 | 0.18196 | 0.19079 | 0.19949 | 0.20807 | 0.21653 | 0.22489 | 0.23314 | 0.2413 | 0.24937
delT | 2.5518 | 2.8893 | 3.2159 | 3.533 | 3.842 | 4.1436 | 4.4387 | 4.7279 | 5.0116 | 5.2904 | 5.5646 | 5.8346 | 6.1006 | 6.3629 | 6.6217 | 6.8772 | 7.1297 | 7.3792 | 7.6259
T head | 18.4482 | 18.1107 | 17.7841 | 17.467 | 17.158 | 16.8564 | 16.5613 | 16.2721 | 15.9884 | 15.7096 | 15.4354 | 15.1654 | 14.8994 | 14.6371 | 14.3783 | 14.1228 | 13.8703 | 13.6208 | 13.3741
Min allowed C | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Height from entry point of cold air to critical point | 0.9 | m |  | SECONDARY SCHOOL PASS/FAIL CALCULATOR (Michael Middleton)
|  |  |  | 5 deg C y intercept 1.4m from floor |  |  |  | 15.6293
Top hung window | 0 |  |  | Minimum temperature allowed |  |  |  | 16
Bottom hung hopper window | 0.4 |  |  | Result |  |  |  | Fail
Damper | 0.1
Distance added | 0
Average temperature of classroom | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
5C dotted line | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
PRIMARY SCHOOLS
alpha T | 0.08 | (standard value would be 0.102 but following discussion with Malcolm Cook in Dec 2016, and subsequent discussions with Paul Linden, Malcolm Cook, Henry Burridge, David Parker, Colm-cille Caulfield, Owen Connick and Shaun Fitzgerald in Mar 2018 it was agreed this should be reduced to 0.08)
C | 0.085668 | (not used)
Vl source | 0.032 | cu m/s/m
T ext | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3
g prime source | 0.1962 | 0.2289 | 0.2616 | 0.2943 | 0.327 | 0.3597 | 0.3924 | 0.4251 | 0.4578 | 0.4905 | 0.5232 | 0.5559 | 0.5886 | 0.6213 | 0.654 | 0.6867 | 0.7194 | 0.7521 | 0.7848
Bo | 0.0075341 | 0.0087898 | 0.010045 | 0.011301 | 0.012557 | 0.013812 | 0.015068 | 0.016324 | 0.01758 | 0.018835 | 0.020091 | 0.021347 | 0.022602 | 0.023858 | 0.025114 | 0.026369 | 0.027625 | 0.028881 | 0.030136
h virtual origin | 0.66273 | 0.62957 | 0.60219 | 0.57903 | 0.55906 | 0.5416 | 0.52613 | 0.51229 | 0.4998 | 0.48845 | 0.47807 | 0.46851 | 0.45968 | 0.45148 | 0.44383 | 0.43668 | 0.42997 | 0.42365 | 0.41769
g prime floor | 0.070005 | 0.078988 | 0.087653 | 0.096048 | 0.10421 | 0.11216 | 0.11992 | 0.12751 | 0.13496 | 0.14226 | 0.14943 | 0.15649 | 0.16343 | 0.17027 | 0.17701 | 0.18366 | 0.19023 | 0.19671 | 0.20312
delT | 2.1408 | 2.4155 | 2.6805 | 2.9372 | 3.1867 | 3.4298 | 3.6673 | 3.8995 | 4.1271 | 4.3504 | 4.5698 | 4.7855 | 4.9979 | 5.207 | 5.4132 | 5.6167 | 5.8174 | 6.0157 | 6.2117
T head | 18.8592 | 18.5845 | 18.3195 | 18.0628 | 17.8133 | 17.5702 | 17.3327 | 17.1005 | 16.8729 | 16.6496 | 16.4302 | 16.2145 | 16.0021 | 15.793 | 15.5868 | 15.3833 | 15.1826 | 14.9843 | 14.7883
Min allowed C | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Height from entry point of cold air to critical point | 1.2 | m |  | PRIMARY SCHOOL PASS/FAIL CALCS (Michael Middleton)
|  |  |  | % deg C y intercept 1.1m from floor |  |  |  | 16.5976
Top hung window | 0 |  |  | Minimum temperature allowed |  |  |  | 16
Bottom hung hopper window | 0.4 |  |  | Result |  |  |  | Pass
Damper | 0.1
Distance added | 0